Research spike update – Greenville Utilities Commission focus manufacturer manuals reviewed

Source upgrade: The approach was revised and the goal is to pull from Greenville Utilities Commission (GUC’s) approved vender list rather than obtaining generic IEC standards. The primary manual that was reviewed is Howard Industries HI-105 (three phase pad mounted, 45-10,000 kVA). The secondary reference includes Prolec GE three phase pad mount IOM. The manual pages for Howard HI-105 Sections 4, 5, and 6 are available at

http://w.howard-ind.com/HowardTransformers/Literature/ThreePhasePadmountedTransformerInstructionManual.pdf

Are the thresholds simple scalars, or per-component, or load-dependent?

The thresholds are per-component, the fluid temp, arrester limits and winding hotspots are all going to be different. Overloads are load dependent per ANSI C57.92.

Are they absolute temps (C) or relative to ambient (T)?

Both, the normal operating ceiling is expressed as T (ambient temperature + 85C rise). Arrester limits are absolute.

Are severity tiers defined (normal/warning / critical)?

No both Howard and Prolec define a normal ceiling only. Warning/alarm/critical tiers live in GUC’s SCADA setpoints, not the manufacturer manuals. Any of this information may require a direct call to a GUC engineer.

Are these separate thresholds for different transformer types?

Yes for fluid type it matters as the mineral oil, R-temp and FR3 have different minimum operating temperatures. kVA size affects rated raise.

Extracted Data

| Component | Threshold Type | Value | Source |
| --- | --- | --- | --- |
| Top-oil (normal operation) | T above ambient | Ambient + 85C | Howard HI-105 Section 6 |
| Top-oil (Greenville Summer Estimate) | Absolute Ceiling | 120C | Derived: 35C ambient + 85C |
| MOV surge arrester (recommended) | Absolute | 90C average oil | Howard HI-105 Section 5 |
| MOV Surge arrester (Max) | Absolute | 125C | Howard HI-105 Section 5 |
| Min fluid temp for energizing (mineral oil) | Absolute floor | -20C | Howard HI-105 Section 4 |
| Min fluid temp for energizing (R-temp) | Absolute floor | 0C | Howard HI-105 Section 4 |
| Min fluid temp for energizing (FR3) | Absolute floor | -10C | Howard HI-105 Section 4 |
| Winding hit-spot/overload limits | - | Deferred to IEEE C57.91/ ANSI C57.92 | Howard HI-105 + Prolec GM IOM |

The key finding for HER-80: The thermal camera reads the external tank surface, not the oil. Tank surface  top oil -10 to 15 C under normal conditions. This translation layer needs to be accounted for in pipeline design.

Still missing: GUC SCADA alarm setpoints (actual warning/alarm/critical tiers). A call to GUC engineering may allow us to unblock this and have this data.

Blocks: May block ticket HER-80 pending SCADA setpoints, HER-81 confirmed as hard dependent.

Key Terms Highlighted:

International Electrotechnical Commission (IEC): Global standards that writes technical standards for electrical and electronic equipment. EX published “IEC 60###”.

Installation, Operation, and Maintenance manual (IOM): Name manufacturer ships their equipment, official manual covering how to install it how to run it day by day and how to service.

ANSI C57.92: C57 is the series specifically covering transformers. 92 is the specific document within series which covers guidelines for how much you can overload a transformer and how long before starts taking damage.

Supervisory Control and Data Acquisition: Software and hardware system a utility like GUC uses to remotely monitor and control their entire grid in real time. Transformers, switches, voltage levels etc.